## Pump 1
C.W. Pump 1
[6 empty] | Hue: |  |  | 39
Enter Following Details: | [5 empty] | Saturation: |  | 82
|  |  | Rated Values |  |  | Luminance: |  | 46
Flow rate of pump | 1220 | m3/hr | 1400 |  |  | Contrast: |  | 50
Discharge Head | 28 | m | 25
Suction Head | 2.5 | m | 0 | [11 empty] | Energy Saving Opportunities
Pipe diameter | 60 | in | [8 empty] | Comparison Sheet |  |  |  |  | Flow (m3/hr) | Head (m) | Motor Power (kW) | Pump Efficiency (%) | %age Loading over motor
| 1.524 | m |  | Motor Power consumption | 119.0211 | kW |  |  |  |  | Flow (m3/hr) | Head (m) | Power (kW) | Efficiency (%) | Designed Conditions | 1400 | 25 | 132 | 85.16%
Physical Properties of fluid: |  |  |  | Water kW | 84.6883 | kW |  |  |  | Actual | 1220 | 25.5 | 119.0211 | 79.06% | Actual Conditions | 1220 | 25.5 | 119.0211 | 79.06% | 90.17%
Type of fluid | Water |  |  | Motor Loss | 11.9021 | kW | 10% |  |  | Designed | 1400 | 25 | 132 | 85.16% | Proposed System | 1220 | 25.5 | 116.5302 | 85% | 90%
Density of fluid | 1000 | kg/m3 |  | kW delivered to pump | 107.119 | kW
Viscosity of fluid | 1 | cP |  | Overall System Efficiency | 71.154 | %
Temperature of fluid | 31 | deg C |  | Pump Efficiency | 79.06% | [10 empty] | Saving |  | 14.144 | kW
|  |  |  | Eff. Acc. To Rated values | 85.16% | [10 empty] | Operating Hours |  | 7920 | Hours
Electrical Measurements: |  |  |  | Loss due to pump Inefficiency | 22.4307 | kW | 18.85% | [8 empty] | Unit Price |  | 2 | Rs./kWh
Voltage | 426.072 | Volts |  | Loss due to throttling | 0 | kW | 0% | [8 empty] | Monetary Saving | Rs. | 2.2404 | Lacs Per annum
Current | 192 | Amps |  | kW after pump | 84.6883 | kW
Power factor | 0.84 | 119.0211 |  | Actual Water kW | 84.6883 | kW | [9 empty] | Saving by avoiding Throttling Losses |  | 0 | kW
Motor Power consumption | 119.0211 | kW | [13 empty] | Monetary saving | Rs. | 0 | Lacs per annum
Motor Efficiency | 90 | % |  | kW/m3 | 0.097558
Rated Power | 132 | kW | 132 | Velocity of water | 0.18578 | m/s | [9 empty] | Total Saving | Rs. | 2.2404 | Lacs per annum
Loading %age | 90.17%
Throttling %age | 0 | %
Head drop across valve | 0 | m
Loss due to throttling | 0 | kW
PROPOSED SYSTEM
Proposed flow | 1220
Proposed Head | 25.5
Pump Efficiency | 85%
Proposed Motor kW | 116.5302 | 93 % Eff of motor, 90% Loading
Loading over Motor (%age) | 90%
Note on G3: Saturation: 0 - Grayscale 100 - Full Color
Note on G2: HUE: The hue is associated with the color strip above the scroll bar. Values range from 0 to 255
Note on G4: Luminance (brightness): 0 - Dark 100 - Light
Note on G5: Contrast: 0 - Washed Out 100 - Extreme Contrast This template creates two arrays of 5 colors ranging from dark to light. The Luminance (brightness) controls the middle value and the contrast controls the values of the other colors.
119.0
107.1
84.7
84.7
11.9
kW
kW
kW
Motor loss
10%
Pump loss
22.4
kW
19%
Throttling loss
0.0
kW
0%
kW
kW
Pump Efficiency
79%

## Pump3
C.W. Pump 3
[6 empty] | Hue: |  |  | 39
Enter Following Details: | [5 empty] | Saturation: |  | 82
|  |  | Rated Values |  |  | Luminance: |  | 46
Flow rate of pump | 1310 | m3/hr | 1400 |  |  | Contrast: |  | 50
Discharge Head | 26 | m | 25
Suction Head | 2.5 | m | 0 | [11 empty] | Energy Saving Opportunities
Pipe diameter | 60 | in | [8 empty] | Comparison Sheet |  |  |  |  | Flow (m3/hr) | Head (m) | Motor Power (kW) | Pump Efficiency (%) | %age Loading over motor
| 1.524 | m |  | Motor Power consumption | 114.2946 | kW |  |  |  |  | Flow (m3/hr) | Head (m) | Power (kW) | Efficiency (%) | Designed Conditions | 1400 | 25 | 132 | 85.16%
Physical Properties of fluid: |  |  |  | Water kW | 83.8036 | kW |  |  |  | Actual | 1310 | 23.5 | 114.2946 | 81.47% | Actual Conditions | 1310 | 23.5 | 114.2946 | 81.47% | 86.59%
Type of fluid | Water |  |  | Motor Loss | 11.4295 | kW | 10% |  |  | Designed | 1400 | 25 | 132 | 85.16% | Proposed System | 1310 | 23.5 | 115.3128 | 85% | 90%
Density of fluid | 1000 | kg/m3 |  | kW delivered to pump | 102.8651 | kW
Viscosity of fluid | 1 | cP |  | Overall System Efficiency | 73.3225 | %
Temperature of fluid | 25 | deg C |  | Pump Efficiency | 81.47% | [10 empty] | Saving |  | 10.513 | kW
|  |  |  | Eff. Acc. To Rated values | 85.16% | [10 empty] | Operating Hours |  | 7920 | Hours
Electrical Measurements: |  |  |  | Loss due to pump Inefficiency | 19.0615 | kW | 16.68% | [8 empty] | Unit Price |  | 2 | Rs./kWh
Single Phase Voltage | 423 | Volts |  | Loss due to throttling | 0 | kW | 0% | [8 empty] | Monetary Saving | Rs. | 1.6653 | Lacs Per annum
Current | 195 | Amps |  | kW after pump | 83.8036 | kW
Power factor | 0.8 | 114.2946 |  | Actual Water kW | 83.8036 | kW | [9 empty] | Saving by avoiding Throttling Losses |  | 0 | kW
Motor Power consumption | 114.2946 | kW | [13 empty] | Monetary saving | Rs. | 0 | Lacs per annum
Motor Efficiency | 90 | % |  | kW/m3 | 0.087248
Rated Power | 132 | kW | 132 | Velocity of water | 0.19948 | m/s | [9 empty] | Total Saving | Rs. | 1.6653 | Lacs per annum
Loading %age | 86.59%
Throttling %age | 0 | %
Head drop across valve | 0 | m
Loss due to throttling | 0 | kW
PROPOSED SYSTEM
Proposed flow | 1310
Proposed Head | 23.5
Pump Efficiency | 85%
Proposed Motor kW | 115.3128 | 93 % Eff of motor, 90% Loading
Loading over Motor (%age) | 90%
Note on G3: Saturation: 0 - Grayscale 100 - Full Color
Note on G2: HUE: The hue is associated with the color strip above the scroll bar. Values range from 0 to 255
Note on G4: Luminance (brightness): 0 - Dark 100 - Light
Note on G5: Contrast: 0 - Washed Out 100 - Extreme Contrast This template creates two arrays of 5 colors ranging from dark to light. The Luminance (brightness) controls the middle value and the contrast controls the values of the other colors.
114.3
102.9
83.8
83.8
11.4
kW
kW
kW
Motor loss
10%
Pump loss
19.1
kW
17%
Throttling loss
0.0
kW
0%
kW
kW
Pump Efficiency
81%

## CT Pumps Design Details
I) NEW COOLING TOWER & PUMP HOUSE
Sr. | Eqpt No | Equipment Name | KW | RPM | FLC | Make | SL. NO.
1 |  | Cooling Water Pump-1 | 132 | 1483 | 220 | KEC | 29808037-6
2 |  | Cooling Water Pump-2 | 132 | 1485 | 228 | ALSTOM | 24560300011
3 |  | Cooling Water Pump-3 | 132 | 1483 | 220 | KEC | 29811044-1
4 |  | Cooling Water Pump-4 | 132 | 1485 | 228 | ALSTOM | 24560300012

## CT Design Details
New Cooling Tower Desing Details
Parameters | Value | Unit
Type | Cross Flow , Timber Tower
Tower Model | 596-8V-4
No. of Cells | 3 (Working) + 1 (Standby)
Rated Circulating Water Flow | 4560 | m3/hr
Rated Cooling Water Flow | 6080 | m3/hr
Hot Water Inlet Temp | 42 | deg C
Cold Water O/L Temp | 33 | deg C
Designed Wet Bulb Temp | 28 | deg C