## Booster Pump
[5 empty] | PROJECT :Installation of new booster pump/Removal of existing booster pump in Compressor House. | [6 empty] | Design details of the booster pumps are mentioned in the table below: |  |  |  |  | PROPOSAL: |  |  |  |  | COST BENEFIT ANALYSIS: | [6 empty] | OTHER BENEFITS: |  | BASE LINE PARAMETERS: |  |  |  |  | PMV OPTION: Retrofit Isolation
| PROJECT DOCUMENT |  | Contents | [9 empty] | S.No. | Particular | Value | Units | Booster pump's performance was checked. The details are in the following table:
[13 empty] | 1 | Make | TSP | [6 empty] | The results and saving analysis are as follows: | [6 empty] | 1) | Maintainance of pump will be avoided. |  | S.No. | Particular | Value | Units | M & V PLAN:
|  | S.No. | Contents | Page No. | EXISTING SITUATION: | [7 empty] | 2 | Flow | 330 | m3/hr | [5 empty] | Present Scenario: | [6 empty] | 2) | Pressure drop across the pump will be avoided & flow rate will improve. |  | 1 | Power cost | 2 | Rs./kWh |  | OPTION 1:
|  | 1 | Project description |  | Compressor house consists of 5 numbers of compressors. All are two stage compressors. For intercooling the cooling water is supplied through cooling tower. ACW Pump pumps the water for the generator air coolers, oil coolers and for compressor house intercoolers and aftercoolers. One booster pump is installed in between ACW pump discharge and before compressor for increasing flow. The temperature across the compressors are measured when booster pump is on and when it is switched off. The results are as below: | [7 empty] | 3 | Total Head | 25 | m | [6 empty] | S.No. | Particular |  |  | Value | Units |  |  |  | 2 | Operating days | 330 | days | BEFORE IMPLEMENTATION |  |  |  | AFTER IMPLEMENTATION
PROJECT :Installation of new booster pump/Removal of existing booster pump in Compressor House. |  | 2 | Existing situation | [9 empty] | 4 | Power | 22 | kW | [6 empty] | 1 | Flow rate |  |  | 60 | m3/hr |  |  |  | 3 | Operating Hours | 24 | Hours/day | S.No. | Parameters | Value | Unit | S.No. | Parameters | Value | Unit
|  | 3 | Proposal | [19 empty] | 2 | Total Head |  |  | 28 | m | [7 empty] | 1 | Power consumption | 19.27 | kW | 1 | Power consumption |  | kW
|  | 4 | Cost Benefit Analysis | [19 empty] | 3 | Power consumption |  |  | 19.27 | kW | [7 empty] | 2 | Operating Hours | 7920 | Hrs/yr | 2 | Operating Hours | 7920 | Hrs/yr
|  | 5 | Other Benefits | [13 empty] | OPTION 1: Replacement of old inefficient pump with New pump of High Efficiency. | [5 empty] | 5 | Operating Hours |  |  | 7920 | Hours | [7 empty] | 3 | Units consumption | 152618.4 | kWh/yr | 3 | Units consumption |  | kWh/yr
| Paste Company Picture Here | 6 | Baseline parameters | [19 empty] | 6 | Total Units consumption |  |  | 1.5262 | Lacs per annum | [7 empty] | 4 | Energy cost | 305236.8 | Rs./yr | 4 | Energy cost |  | Rs./yr
|  | 7 | PMV Option | [14 empty] | New pump Specifications: |  |  |  |  | 7 | Annual Energy Cost |  |  | 3.0524 | Rs. Lacs
|  | 8 | M & V Plan | [14 empty] | S.No. | Particular | Value | Units
[5 empty] | Time | Booster Pump On |  | Booster Pump Off |  | Temp. Diff. across compressor House | [7 empty] | 1 | Flow | 80 | m3/hr | Proposed System: | [13 empty] | Saving (Rs./Yr) = (Energy Cost (Rs./yr) before Implementation - Energy Cost(Rs/yr) after Implementation)
[6 empty] | I/L Temp (deg C) | O/L Temp (deg C) | I/L Temp (deg C) | O/L Temp (deg C) | [8 empty] | 2 | Total Head | 30 | m |  | OPTION 1: Replacement of old pump with New high efficiency pump.
[10 empty] | B.P. On | B.P. Off | [6 empty] | 3 | New Power consumption | 9.81 | kW |  | S.No. | Particular |  |  | Value | Units
[23 empty] | 1 | Flow rate |  |  | 80 | m3/hr
[5 empty] | 26/7/06 | [17 empty] | 2 | Total Head |  |  | 30 | m
[5 empty] | 15:30 | 32.5 | 39 | 32.5 | 41 | 6.5 | 8.5 | [5 empty] | OPTION 2: Switching off the Booster Pump. | [5 empty] | 3 | Power consumption |  |  | 9.81 | kW
[5 empty] | 18:30 | 32 | 39 | 32 | 40 | 7 | 8 | [5 empty] | The temperatures were measured during different times in a days. The results shows that the temperature rise in case the booster pump is switched off, is 1 to 2 deg C more than when it is running. The temperature rise is not much so the booster pump can be avoided. | [5 empty] | 5 | Operating Hours |  |  | 7920 | Hours
[5 empty] | 21:00 | 31 | 38.5 | 31 | 39.5 | 7.5 | 8.5 | [11 empty] | 6 | Total Units consumption |  |  | 0.77695 | Lacs per annum
[23 empty] | 7 | Annual Energy Cost |  |  | 1.5539 | Rs. Lacs
27/7/06
[5 empty] | 9:30 | 31.5 | 38 | 31.5 | 39 | 6.5 | 7.5 | [11 empty] | Power saving: |  | 9.46 | kW
[5 empty] | 13:00 | 32 | 38.5 | 32 | 39 | 6.5 | 7 | [11 empty] | Monetary saving: |  | 1.4985 | Rs. Lacs per annum
[23 empty] | Investment : |  | 1 | Rs. Lacs
[5 empty] | There is one to two degree rise in temperature when the booster pump is switched off. | [17 empty] | Payback: |  | 8.0082 | Months
Figure below shows the booster pump and it's purpose.
OPTION 2: Switching off the Booster Pump.
[23 empty] | Power saving: |  | 19.27 | kW
| RAMA NEWSPRINT & PAPERS LTD. (RNPL) | [21 empty] | Monetary saving: |  | 3.0524 | Rs. Lacs per annum
[23 empty] | Investment : |  | Nil
[23 empty] | Payback: |  | Immediate
DSCL ENERGY SERVICES COMPANY LTD.
II Floor, Kanchenjunga, 18 Barakhamba Road, New Delhi –110 001